## AD_MOTS
FUNCTION ACTIVATED ON BAMOWIZ
| Adress F3 / F4 | Bits | LEVEL | VOLUME | SPECIFIC | FREQUENCY
Floating number on 4 bytes | 40001 | b7 … b0 | mm Input 1 | mm Input 1 | Input 1 (sensor unit)
b15 … b8
| 40002 | b23 … b16
b31 … b24
| 40003 | b7 … b0 | mm Input 2 | mm Input 2 | Input 2 (sensor unit)
b15 … b8
| 40004 | b23 … b16
|  | b31 … b24 | [9 empty] | FUNCTION
| 40005 | b7 … b0 | mm Input 3 / differential | mm Input 3 / differential | Input 3 / differential (sensor unit) | IMPULSES |  |  |  | Adress | Bits | level | volume | specific | frequency
|  | b15 … b8 | [7 empty] | 40001 | b7 … b0
| 40006 | b23 … b16 | [8 empty] | b15 … b8
|  | b31 … b24 | [7 empty] | 40002 | b23 … b16
| 40007 | b7 … b0 | % lev Input 1 | % niv Input 1 | Input 1 (linearization unit) | [5 empty] | b31 … b24
|  | b15 … b8 | [7 empty] | 40003 | b7 … b0
| 40008 | b23 … b16 | [8 empty] | b15 … b8
|  | b31 … b24 | [7 empty] | 40004 | b23 … b16
| 40009 | b7 … b0 | % lev Input 2 | % niv Input 2 | Input 2 (linearization unit) | [5 empty] | b31 … b24
|  | b15 … b8 | [7 empty] | 40005 | b7 … b0
| 40010 | b23 … b16 | [8 empty] | b15 … b8
|  | b31 … b24 | [7 empty] | 40006 | b23 … b16
| 40011 | b7 … b0 | % lev Input 3 / differential | % niv Input 3 / differential | Input 3 / differential (linearization unit) | TOTALIZATION |  |  |  |  | b31 … b24
|  | b15 … b8 | [7 empty] | 40007 | b7 … b0
| 40012 | b23 … b16 | [8 empty] | b15 … b8
|  | b31 … b24 | [7 empty] | 40008 | b23 … b16
| 40013 | b7 … b0 | 0 | m3 Input 1 | 0 | [5 empty] | b31 … b24
b15 … b8
| 40014 | b23 … b16
b31 … b24
| 40015 | b7 … b0 | 0 | m3 Input 2 | 0
b15 … b8
| 40016 | b23 … b16
b31 … b24
| 40017 | b7 … b0 | 0 | m3 Input 3 / differential | 0
b15 … b8
| 40018 | b23 … b16
b31 … b24
| 40019 | b7 … b0 | 0 | % vol Input 1 | 0
b15 … b8
| 40020 | b23 … b16
b31 … b24
| 40021 | b7 … b0 | 0 | % vol Input 2 | 0
b15 … b8
| 40022 | b23 … b16
b31 … b24
| 40023 | b7 … b0 | 0 | % vol Input 3 / differential | 0
b15 … b8
| 40024 | b23 … b16
b31 … b24
| 40025 | b7 … b0 | VALUE N°1 OF INPUT 1
b15 … b8
| 40026 | b23 … b16
b31 … b24
| 40027 | b7 … b0 | VALUE N°1 OF INPUT 2
b15 … b8
| 40028 | b23 … b16
|  | b31 … b24 | [5 empty] | Bits
| 40029 | b7 … b0 | VALUE N°1 OF INPUT 3 / DIFFERENTIAL |  |  | VALUE OF IMPULSES / TOTALIZATION |  |  |  |  | ON | OFF
|  | b15 … b8 |  |  |  |  | Relays / visual alarm | 0 | relay 1 active? |  | 1 | 0
| 40030 | b23 … b16 | [5 empty] | 1 | relay 1 current state
|  | b31 … b24 | [5 empty] | 2 | relay 2 active? |  | Closed | Open
| 40031 | b7 … b0 | VALUE N°2 OF INPUT 1 |  |  |  |  | 3 | relay 2 current state |  | 1 | 0
|  | b15 … b8 | [5 empty] | 4 | relay 3 active?
| 40032 | b23 … b16 | [5 empty] | 5 | relay 3 current state
|  | b31 … b24 | [5 empty] | 6 | reserved
| 40033 | b7 … b0 | VALUE N°2 OF INPUT 2 |  |  |  |  | 7 | reserved
|  | b15 … b8 | [5 empty] | 8 | reserved
| 40034 | b23 … b16 | [5 empty] | 9 | reserved
|  | b31 … b24 | [5 empty] | 10 | reserved
| 40035 | b7 … b0 | VALUE N°2 OF INPUT 3 / DIFFERENTIAL |  |  | VALUE OF IMPULSES |  | 11 | reserved
|  | b15 … b8 | [5 empty] | 12 | reserved
| 40036 | b23 … b16 | [5 empty] | 13 | reserved
|  | b31 … b24 | [5 empty] | 14 | Visual Alarm active ? |  | Active | Inactive
| 40037 | b7 … b0 | RELAY / VISUAL ALARM (also available bit by bit with function 1 or 2) |  |  |  |  | 15 | Vis Al current state |  | 1 | 0
b15 … b8
| 40038 | b7 … b0 | THRESHOLDS 1 to 8 (also available bit by bit with functions 1 or 2) |  |  |  |  | Bits
b15 … b8
| 40039 | b7 … b0 | reserved |  |  |  | THRESHOLDS 1 to 8 | 0 | S1 Active? |  | Active | Inactive
|  | b15 … b8 | [5 empty] | 1 | S1 active / Inactive |  | 1 | 0
Characters strings | 40040 | b7 … b0 | VALUE n°1 OF INPUT 1 in ASCII (as displayed) |  |  |  |  | 2 | S2 Active?
|  | b15 … b8 | [5 empty] | 3 | S2 active / Inactive
| 40041 | b7 … b0 | [5 empty] | 4 | S3 Active?
|  | b15 … b8 | [5 empty] | 5 | S3 active / Inactive
| 40042 | b7 … b0 | [5 empty] | 6 | S4 Active?
|  | b15 … b8 | [5 empty] | 7 | S4 active / Inactive
| 40043 | b7 … b0 | VALUE n°1 of INPUT 2 in ASCII (as displayed) |  |  |  |  | 8 | S5 Active?
|  | b15 … b8 | [5 empty] | 9 | S6 active / Inactive
| 40044 | b7 … b0 | [5 empty] | 10 | S6 Active?
|  | b15 … b8 | [5 empty] | 11 | S6 active / Inactive
| 40045 | b7 … b0 | [5 empty] | 12 | S7 Active?
|  | b15 … b8 | [5 empty] | 13 | S7 active / Inactive
| 40046 | b7 … b0 | VALUE N°1 OF INPUT 3 / DIFFERENTIAL in ASCII (as displayed) |  |  | VALUE OF IMPULSES / TOTALIZATION in ASCII (as displayed) |  | 14 | S8 Active?
|  | b15 … b8 | [5 empty] | 15 | S8 active / Inactive
| 40047 | b7 … b0
b15 … b8
| 40048 | b7 … b0
b15 … b8
| 40049 | b7 … b0 | VALUE n°2 OF INPUT 1 in ASCII (as displayed)
b15 … b8
| 40050 | b7 … b0
b15 … b8
| 40051 | b7 … b0
b15 … b8
| 40052 | b7 … b0 | VALUE n°2 OF INPUT 2 in ASCII (as displayed)
b15 … b8
| 40053 | b7 … b0
b15 … b8
| 40054 | b7 … b0
b15 … b8
| 40055 | b7 … b0 | VALUE N°2 OF INPUT 3 / DIFFERENTIAL in ASCII (as displayed) |  |  | VALUE OF IMPULSES in ASCII (as displayed)
b15 … b8
| 40056 | b7 … b0
b15 … b8
| 40057 | b7 … b0
b15 … b8
| 40058 | b7 … b0 | UNIT OF INPUT 1 - VALUE N°1 in ASCII (as displayed)
b15 … b8
| 40059 | b7 … b0
b15 … b8
| 40060 | b7 … b0
b15 … b8
| 40061 | b7 … b0
b15 … b8
| 40062 | b7 … b0
b15 … b8
| 40063 | b7 … b0 | UNIT OF INPUT 2 - VALUE N°1 in ASCII (as displayed)
b15 … b8
| 40064 | b7 … b0
b15 … b8
| 40065 | b7 … b0
b15 … b8
| 40066 | b7 … b0
b15 … b8
| 40067 | b7 … b0
b15 … b8
| 40068 | b7 … b0 | UNIT OF INPUT 3 / DIFFERENTIAL - VALUE N°1 in ASCII (as displayed) |  |  | UNIT OF IMPULSES / TOTALIZATION in ASCII (as displayed)
b15 … b8
| 40069 | b7 … b0
b15 … b8
| 40070 | b7 … b0
b15 … b8
| 40071 | b7 … b0
b15 … b8
| 40072 | b7 … b0
b15 … b8
| 40073 | b7 … b0 | UNIT OF INPUT 1 - VALUE N°2 in ASCII (as displayed)
b15 … b8
| 40074 | b7 … b0
b15 … b8
| 40075 | b7 … b0
b15 … b8
| 40076 | b7 … b0
b15 … b8
| 40077 | b7 … b0
b15 … b8
| 40078 | b7 … b0 | UNIT OF INPUT 2 - VALUE N°2 in ASCII (as displayed)
b15 … b8
| 40079 | b7 … b0
b15 … b8
| 40080 | b7 … b0
b15 … b8
| 40081 | b7 … b0
b15 … b8
| 40082 | b7 … b0
b15 … b8
| 40083 | b7 … b0 | UNIT OF INPUT 3 / DIFFERENTIAL - VALUE N°2 in ASCII (as displayed) |  |  | UNIT OF IMPULSES in ASCII (as displayed)
b15 … b8
| 40084 | b7 … b0
b15 … b8
| 40085 | b7 … b0
b15 … b8
| 40086 | b7 … b0
b15 … b8
| 40087 | b7 … b0
b15 … b8
HOW TO USE ?
THIS
Is the information you get when you configure your MODBUS client to retrieve data at
THIS ADRESS while
THIS FUNCTION is selected on the BAMOWIZ
GLOSSARY
"As displayed" = when retrieving data in ASCII format, you get the exact same thing that is displayed real time on BAMOWIZ screen
"Differential" = when using the "differential" function on the BAMOWIZ (I1 - I2)
"Value n°1" = refers to the value of numeric display. Explicitely referred to as "Display n°1" in BAMOWIZ configuration menu.
"Value n°2" = refers to the value of graphic display. Explicitely referred to as "Display n°2" in BAMOWIZ configuration menu.
WE DO NOT PROVIDE MODBUS CLIENT
RS485 MODBUS is open &
compatible with any client solution suitable for this protocol

## AD_BITS
Adresse F1 / F2
|  |  | ON | OFF
Relais / Alarme Visuel | 1 | Relais 1 Activé? | 1 | 0
| 2 | Relais 1 Etat
| 3 | Relais 2 Activé? | Fermé | Ouvert
| 4 | Relais 2 Etat | 1 | 0
| 5 | Relais 3 Activé?
| 6 | Relais 3 Etat
| 7 | réserve
| 8 | réserve
| 9 | réserve
| 10 | réserve
| 11 | réserve
| 12 | réserve
| 13 | réserve
| 14 | réserve
| 15 | Al. Visuel Activée? | Active | Inactive
| 16 | Al. Visuel Etat | 1 | 0
Adresse F1 / F2
SEUILS 1 à 8 | 17 | S1 Activé? | Actif | Inactif
| 18 | S1 Actif / Inactif | 1 | 0
| 19 | S2 Activé?
| 20 | S2 Actif / Inactif
| 21 | S3 Activé?
| 22 | S3 Actif / Inactif
| 23 | S4 Activé?
| 24 | S4 Actif / Inactif
| 25 | S5 Activé?
| 26 | S6 Actif / Inactif
| 27 | S6 Activé?
| 28 | S6 Actif / Inactif
| 29 | S7 Activé?
| 30 | S7 Actif / Inactif
| 31 | S8 Activé?
| 32 | S8 Actif / Inactif